## Published Version
Subtransmission Substation / Zone Substation / Modular Substation | Power Transformer | Nameplate Rating (MVA) | Power Transformer Cyclic Ratings (MVA) |  |  | Comments
|  |  | Normal Cyclic | *Long Term Emergency | *Short Term Emergency
|  |  |  | (4 hours) | (up to 1 hour)
Archer | TF 1 | 20/27 | 30.9 | 36.2 | 38.1 | The short term emergency cyclic rating is limited by the CT ratio, 11kV circuit breaker and busbar rating.
| TF 2 | 20/27 | 30.9 | 36.2 | 38.1 | The short term emergency cyclic rating is limited by the CT ratio, 11kV circuit breaker and busbar rating.
Batchelor | TF 1 | 20/27 | 25.378 | 26.7865 | 28.1696 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 22kV power transformer cables.
Berrimah | TF 1 | 25/31.5/38 | 24.372 | 30.465 | 33.8162 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 11kV power transformer cables.
| TF 2 | 25/31.5/38 | 24.372 | 30.465 | 33.8162 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 11kV power transformer cables.
Brewer | TF 1 | 12/15 | 8.124 | 10.155 | 11.2721 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 11kV power transformer cables.
Casuarina | TF 1 | 20/27 | 29.5 | 35.1 | 35.1 | The cyclic ratings (long term and short term emergency) are limited by the CT ratio.
| TF 2 | 20/27 | 29.5 | 35.1 | 35.1 | The cyclic ratings (long term and short term emergency) are limited by the CT ratio.
| TF 3 | 20/27 | 29.5 | 35.1 | 35.1 | The cyclic ratings (long term and short term emergency) are limited by the CT ratio.
Centre Yard | TF 1 | 0.5 | 0.48 | 0.48 | 0.48 | The cyclic ratings (normal, long term and short term emergency) are limited by the power transformer protection settings and power transformer bushing ratings.
| TF 2 | 0.5 | 0.48 | 0.48 | 0.48 | The cyclic ratings (normal, long term and short term emergency) are limited by the power transformer protection settings and power transformer bushing ratings.
Cosmo Howley | TF 1 | 7.5 | 6.1 | 6.1 | 6.1 | The cyclic ratings (normal, long term and short term emergency) are limited by the GCR 0296 protection settings.
| TF 2 | 7.5 | 6.1 | 6.1 | 6.1 | The cyclic ratings (normal, long term and short term emergency) are limited by the GCR 0296 protection settings.
Darwin | TF 1 | 25/31.5/38 | 38.1 | 38.1 | 38.1 | The cyclic ratings (normal, long term and short term emergency) are limited by the CT ratio.
| TF 2 | 25/31.5/38 | 38.1 | 38.1 | 38.1 | The cyclic ratings (normal, long term and short term emergency) are limited by the CT ratio.
| TF 3 | 25/31.5/38 | 38.1 | 38.1 | 38.1 | The cyclic ratings (normal, long term and short term emergency) are limited by the CT ratio.
Frances Bay | TF 1 | 25/31.5/38 | 24.372 | 30.465 | 33.8162 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 11kV power transformer cables.
| TF 2 | 25/31.5/38 | 24.372 | 30.465 | 33.8162 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 11kV power transformer cables.
Hudson Creek | TF 1 | 75/125 | 137.2 | 137.2 | 137.2 | 1.) The cyclic ratings (normal, long term and short term emergency) are limited by the CT ratio. 2.) 'Venus' Overhead conductor limitation 103MVA has not been taken into account, as it is a short span and too much sag is not expected. This conductor needs to be replaced with higher rated conductor in the future.
| TF 2 | 75/125 | 137.2 | 137.2 | 137.2 | 1.) The cyclic ratings (normal, long term and short term emergency) are limited by the CT ratio. 2.) 'Venus' Overhead conductor limitation 103MVA has not been taken into account, as it is a short span and too much sag is not expected. This conductor needs to be replaced with higher rated conductor in the future.
| TF 3 | 75/125 | 137.2 | 137.2 | 137.2 | 1.) The cyclic ratings (normal, long term and short term emergency) are limited by the CT ratio. 2.) 'Venus' Overhead conductor limitation 103MVA has not been taken into account, as it is a short span and too much sag is not expected. This conductor needs to be replaced with higher rated conductor in the future.
Humpty Doo | TF 1 | 2.5 | 2.5 | 2.5 | 2.5 | The cyclic ratings (normal, long term and short term emergency) are limited by the power transformer in poor condition.
| TF 2 | 2.5 | 2.5 | 2.5 | 2.5 | The cyclic ratings (normal, long term and short term emergency) are limited by the power transformer in poor condition.
Katherine | TF1 | 20/33 | 31.8864 | 39.858 | 44.2423 | The cyclic ratings (normal, long term and short term emergency) of the 20/33MVA power transformer are limited by the capacity of 22kV power transformer cables.
| TF2 | 20/27 | 28.6 | 35.5 | 39.6
Leanyer | TF 1 | 20/27 | 30.1 | 30.1 | 30.1 | The cyclic ratings (long term and short term emergency) are limited by the power transformer protection settings.
| TF 2 | 20/27 | 30.1 | 30.1 | 30.1 | The cyclic ratings (long term and short term emergency) are limited by the power transformer protection settings.
Lovegrove 66/22kV | TF 1 | 35/45 | 47.8 | 59.8 | 60.7 | 1.) The cyclic ratings (normal and long term emergency) are limited by capacity of 22kV power transformer cables. 2.) Short term cyclic rating is limited by power transformer protection settings.
| TF 2 | 35/45 | 47.8 | 59.8 | 60.7 | 1.) The cyclic ratings (normal and long term emergency) are limited by capacity of 22kV power transformer cables. 2.) Short term cyclic rating is limited by power transformer protection settings.
Lovegrove 22/11kV | TF 1 | 7.5/10 | 8.8404 | 11.0505 | 11.4315 | 1.) The cyclic ratings (normal and long term emergency) are limited by the capacity of 11kV power transformer cables. 2.) Short term emergency cyclic rating is limited by CT ratio.
| TF 2 | 7.5/10 | 8.8404 | 11.0505 | 11.4315 | 1.) The cyclic ratings (normal and long term emergency) are limited by the capacity of 11kV power transformer cables. 2.) Short term emergency cyclic rating is limited by CT ratio.
| TF 3 | 12/15 | 8.8404 | 11.0505 | 12.266 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 11kV power transformer cables.
Manton | TF 1 | 20/27 | 15.9432 | 19.929 | 22.1212 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 22kV power transformer cables.
Marrakai | TF 1 | 2.5 | 3 | 3.4 | 3.4 | The cyclic ratings (long term and short term emergency) are limited by the power transformer protection settings.
Mary River | TF 1 | 5/7.5 | 6.5 | 6.5 | 6.5 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 22kV power transformer conductor.
Owen Springs | TF 1 | 35/45 | 46.3 | 47.6314 | 47.6314 | 1.) The normal cyclic rating is limited by the capacity of 11kV power transformer cables. 2.)The cyclic ratings (long term and short term emergency) are limited by the CT ratio.
| TF 2 | 35/45 | 46.3 | 47.6314 | 47.6314 | 1.) The normal cyclic rating is limited by the capacity of 11kV power transformer cables. 2.)The cyclic ratings (long term and short term emergency) are limited by the CT ratio.
| TF 3 | 35/45 | 38.1051 | 38.1051 | 38.1051 | 1.) The cyclic ratings (normal, long term and short term emergency) are limited by 11kV power transformer bushings.
Palmerston (66/11 kV) | TF 2 | 30/40 | 24.372 | 30.465 | 33.8162 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 11kV power transformer cables.
| TF 3 | 30/40 | 24.372 | 30.465 | 33.8162 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 11kV power transformer cables.
| TF 5 | 30/40 | 33.8831 | 38.1 | 38.1 | 1.) Normal cyclic rating is limited by the capacity of 11kV power transformer cable. 2.) Long term and short term emergency cyclic ratings are limited by CT ratio.
Palmerston (11/22 kV) | TF 4 | 15/19 | 12.2851 | 15.3564 | 17 | 1.) The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 22kV power transformer cables.
Pine Creek (66/22 kV) | TF 2 | 2.5 | 2.7 | 3.2 | 3.2 | The cyclic ratings (long term and short term emergency) are limited by the power transformer protection settings.
Pine Creek (132/66 kV) | TF 1 | 28/30 | 30 | 30 | 30 | The cyclic ratings (normal, long term and short term emergency) are limited by the power transformer in poor condition.
Pine Creek (66/11 kV) | TF 5 | 20 | 19.1 | 20 | 20 | 1.) The normal cyclic ratings are limited by the capacity of 11kV power transformer cables. 2.) The long term and short term emergency cyclic ratings are limited by the LV bushing rating.
| TF 6 | 20 | 19.1 | 20 | 20 | 1.) The normal cyclic ratings are limited by the capacity of 11kV power transformer cables. 2.) The long term and short term emergency cyclic ratings are limited by the LV bushing rating.
Sadadeen (Ron Goodin 11kV) | TF 1 | 15/19 | 19.1 | 19.1 | 19.1 | The cyclic ratings (normal, long term and short term emergency) are limited by the CT ratio.
| TF 2 | 15/19 | 19.1 | 19.1 | 19.1 | The cyclic ratings (normal, long term and short term emergency) are limited by the CT ratio.
| TF 3 | 20/24 | 23.8 | 23.8 | 23.8 | The cyclic ratings (normal, long term and short term emergency) are limited by the 11SD07 circuit breaker rating.
Strangways | TF 1 | 20/27 | 30 | 35.5 | 39.7
| TF 2 | 20/27 | 30 | 35.5 | 39.7
Tennant Creek | TF 3 | 7.5 | 7.5 | 7.5 | 7.5 | The cyclic ratings (normal, long term and short term emergency) are limited by the power transformer bushing ratings.
| TF 4 | 7.5 | 7.5 | 7.5 | 7.5 | The cyclic ratings (normal, long term and short term emergency) are limited by the power transformer bushing ratings.
Tindal | TF 1 | 4 | 3.8 | 3.8 | 3.8 | The cyclic ratings (normal, long term and short term emergency) are limited by the CT ratio.
| TF 2 | 4 | 3.8 | 3.8 | 3.8 | The cyclic ratings (normal, long term and short term emergency) are limited by the CT ratio.
| TF 3 | 4 | 3.8 | 3.8 | 3.8 | The cyclic ratings (normal, long term and short term emergency) are limited by the CT ratio.
Weddell | TF 1 | 5/7.5 | 7.5 | 9.1 | 9.1 | The cyclic ratings (long term and short term emergency) are limited by the GCR 22WD101 protection settings.
| TF 2 | 5/7.5 | 7.5 | 9.1 | 9.1 | The cyclic ratings (long term and short term emergency) are limited by the GCR 22WD102 protection settings.
| TF 3 | 10/13.5 | 9.3 | 9.3 | 9.3 | The cyclic ratings (normal, long term and short term emergency) are limited by the capacity of 22kV power transformer conductor.
Wishart | TF 1 | 8/12 | 11.7554 | 12 | 12 | 1.) The normal cyclic rating is limited by the capacity of 11kV power transformer cables. 2.) The cyclic ratings (long term and short term emergency) are limited by the 11kV power transformer bushings.
Woolner | TF 1 | 20/27 | 28.9 | 32.4 | 32.4 | The cyclic ratings (long term and short term emergency) are limited by the power transformer protection settings.
| TF 2 | 20/27 | 28.9 | 32.4 | 32.4 | The cyclic ratings (long term and short term emergency) are limited by the power transformer protection settings.
| TF 3 | 20/27 | 28.9 | 32.4 | 32.4 | The cyclic ratings (long term and short term emergency) are limited by the power transformer protection settings.
Notes:
*1.) System Control must contact Asset Management (of Power Services) for utilising the long term and short term emergency cyclic ratings. System Control need to receive the written confirmation from Asset Management regarding the asset condition and act accordingly.
This is mainly to make sure that power transformers are in good condition to run them at specified long term and short term emergency ratings (as tabulated above) during the planned/unplanned outage period in the future.

## Published Document (hidden)
Subtransmission Substation / Zone Substation / Modular Substation | Transformer | Nameplate Rating | Power Transformer Cyclic Ratings |  |  | Comments
|  |  | Normal | Long Term Emergency | Short Term Emergency
|  |  |  | (4 hours) | (up to 1 hour)
Archer | TF 1 | 20/27 | 31.5 | 34 | 34 | 1.) The long term emergency cyclic rating is limited by the 11kV transformer cable type. 2.) The short term emergency cyclic rating is limited by the 11kV transformer cable type.
| TF 2 | 20/27 | 31.5 | 34 | 34 | 1.) The long term emergency cyclic rating is limited by the 11kV transformer cable type. 2.) The short term emergency cyclic rating is limited by the 11kV transformer cable type.
Casuarina | TF 1 | 20/27 | 27.9 | 32.4 | 34 | The short term emergency cyclic rating is limited by the 11kV transformer cable type.
| TF 2 | 20/27 | 27.9 | 32.4 | 34 | The short term emergency cyclic rating is limited by the 11kV transformer cable type.
| TF 3 | 20/27 | 27.9 | 32.4 | 34 | The short term emergency cyclic rating is limited by the 11kV transformer cable type.
Darwin | TF 1 | 25/31.5/38 | 38.5 | 39 | 39 | 1.) The long term emergency cyclic rating is limited by the 11kV transformer cable type. 2.) The short term emergency cyclic rating is limited by the 11kV transformer cable type.
| TF 2 | 25/31.5/38 | 38.5 | 39 | 39 | 1.) The long term emergency cyclic rating is limited by the 11kV transformer cable type. 2.) The short term emergency cyclic rating is limited by the 11kV transformer cable type.
| TF 3 | 25/31.5/38 | 38.5 | 39 | 39 | 1.) The long term emergency cyclic rating is limited by the 11kV transformer cable type. 2.) The short term emergency cyclic rating is limited by the 11kV transformer cable type.
Leanyer | TF 1 | 20/27 | 30 | 30 | 30 | 1.) The normal cyclic rating is limited by the transformer overcurrent protection setting. 2.) The long term emergency cyclic rating is limited by the transformer overcurrent protection setting. 3.) The short term emergency cyclic rating is limited by the transformer overcurrent protection setting.
| TF 2 | 20/27 | 30 | 30 | 30 | 1.) The normal cyclic rating is limited by the transformer overcurrent protection setting. 2.) The long term emergency cyclic rating is limited by the transformer overcurrent protection setting. 3.) The short term emergency cyclic rating is limited by the transformer overcurrent protection setting.
Strangways | TF 1 | 20/27 | 30.3 | 31 | 31 | 1.) The long term emergency cyclic rating is limited by the transformer overcurrent protection setting. 2.) The short term emergency cyclic rating is limited by the transformer overcurrent protection setting.
| TF 2 | 20/27 | 30.3 | 31 | 31 | 1.) The long term emergency cyclic rating is limited by the transformer overcurrent protection setting. 2.) The short term emergency cyclic rating is limited by the transformer overcurrent protection setting.
Woolner | TF 1 | 20/27 | 30.9 | 32 | 32 | 1.) The long term emergency cyclic rating is limited by the transformer overcurrent protection setting. 2.) The short term emergency cyclic rating is limited by the transformer overcurrent protection setting.
| TF 2 | 20/27 | 30.9 | 32 | 32 | 1.) The long term emergency cyclic rating is limited by the transformer overcurrent protection setting. 2.) The short term emergency cyclic rating is limited by the transformer overcurrent protection setting.
| TF 3 | 20/27 | 30.9 | 32 | 32 | 1.) The long term emergency cyclic rating is limited by the transformer overcurrent protection setting. 2.) The short term emergency cyclic rating is limited by the transformer overcurrent protection setting.